Russia
EIP Electrotechnical Company Ltd
301363, 11a, Marx str. Aleksin, Tula region

Тel (fax) 8 (48753) 4-99-52

Moscow
Тel. 8 (495) 926-10-80 (217)
_________________________________________

EIP Electrotechnical Company Ltd
PASSPORT
IP 02 PS
High voltage power supply
IPM-25/15

IPM -25/22

IPM -15/15

IPM -9/15

Contents
	1
	Designation ................................................................................................
	3

	2
	Basic technical data and characteristics ........................………………….
	3

	3
	Supply kit ..............................................................................…………….
	4

	4
	Security measures ..............................................................................……
	4

	5
	Technical maintenance ...............................................................………...
	5

	6
	Transportation and storage .............................................................……...
	6

	7
	Certificate of acceptance....................................................................……
	6

	8
	Certificate of preservation ...........................................................………..
	6

	9
	Warranty ..............................................................………………………..
	7


2

9  Warranty
9.1 The Manufacturer guarantees efficiency of high voltage power supply during all warranty period provided observance of maintenance and storage rules. The maximum term of execution for the warranty is 15 days.

9.2 The warranty length for operation time is 18 months since the date of  commissioning/ The warranty for operation is valid only if the power supply is commissioned by manufacturer during warranty time of storage, provided observance of modes of operation, installed during commissioning works.

9.3 Warranty length of storage is 6 months since the date of supply.

9.4 If the storage period is exceeded, before installation on the site, the power supply must be certified by the manufacturer. In this case the warranty is valid during 24 months since the day of supply.

9.5 In absence of commissioning date in warranty coupon, the warranty assurance begins since the moment of supply. The date of supply is determined by the date of shipment of the power supply to the customer according to consignment note.

9.6 The warranty does not extend to:

- mechanical damage;

- damage caused by natural disaster, fire;

- damage caused by interference of foreign materials, substances, insects;

- damage caused by discrepancy to Government standards for mains supply and telecommunication networks.

The warranty becomes invalid if maintenance rules  stated in technical description and maintenance guide are violated.

	Serial nr.
	Date

of  manufacture
	Date

of supply
	Commissioning date
	Certification date

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


Warranty storage life until:       «______»                               201__.

Warranty operation life until:    «            »                               201__.

7

6  Transportation and storage
6.1 During cargo-handling works and transportation jerks and shocks ARE PROHIBITED.

6.2 Transportation must be implemented only in vertical position. Transportation of IPM in oblique or reclining position is also PROHIBITED.

6.3 IPM must be stored in heated premises with temperatures above + 5 oС and relative humidity not exceeding 80% away from acidic and other vapors causing harmful effects for materials.

7  Certificate of acceptance
High  voltage  power  supply  IPM - 25/15
          (Name of the item)                                      (designation)

Works nr.__________
Manufactured and tested in accordance with technical conditions 3683-009-00220302-96, corresponds to passport data and acknowledged as feasible for operation.

Electro durability of oil  ____  kV.

Manufacture date «_____»____________201__             ____________
                                                                                                     ( МП )
8  Certificate of preservation
High  voltage  power  supply  IPM - 25/15

Works Nr._________
Subject to preservation in JSC “EIP Electrotechnical Сompany”, Ltd
                            (Name or code of the enterprise producing the packing)

in accordance with the requirements provided in normative documentation.
Preservation date                 «_____»_______________201___
Term of preservation            ___________________________

Preservation carried out by   ___________________________

6

1 Designation
1.1 High voltage power supply IPM-25/15, IPM-25/22, IPM-15/15,
IPM-9/15 (further on IPM) is designated for supplying energy for technological installations (e.g. electro dehydrators) at high voltage with the frequency 50 Hz.

1.2 IPM provides:

- power supply of technological installation;

- adjustment of output voltage.
1.3 Сlimatic performance: UHL 1 in Government standard (GOST) 15150-59, (GOST) 15543-70.

1.4 IPM has the rate of implosion protection «advanced reliability against explosion ИПМ» (2), provided by “greasy filler of the casing” according to GOST Р51330.7-99, implosion protection labeling 2ExоIIT6 and can be used in highly explosive areas of class В-1а, В-1g.

The casing of IPM is produced with the rate of protection IP66 according to GOST 14254-80.

1.5 Trademark of the item: IPM-25/15, IPM-25/22, IPM-15/15, IPM 9/15.

1.6 Manufacturer: JSC “EIP Electrotechnical Company”, Ltd.

1.7 Date of issue  "____"_______________201__.

1.8 Works Nr.   _______
2  Basic technical data and characteristics

2.1 Basic technical data and characteristics are given in Table 1.

Table 1
	Names of characteristics
	Nominal characteristics

	
	IPM-25/15
	IPM-25/22
	IPM-15/15
	IPM-9/15

	1 The power supply of IPM is implemented through 2- or 3- phase AC network: 

voltage, V
frequency, Hz
	
[image: image1.wmf]380

10

15

+

-

%

%


50±1

	2 Maximum output voltage, AC, frequency 50 Hz,current value,Umax, kW
	15.0
	22.0
	15.0

	3 Nominal load current, А
	1.5
	0.9
	1.0
	0.6

	4 Output voltage turndown, kW
	 (0,1-1,0) Umax

	
	3

	5 Maximum capacity consumed, not more, kVA
	25.0
	25.0
	15.0
	9.0

	6 Dimensions, mm
	596x416x1075

	7 Weight of IPM without oil, kg
	160
	160
	150
	150

	8The volume of the oil filled. L
	100
	100
	105
	105


2.2 Parallel connection of IPM for one load is allowed, when two equal restriction rates  of load current are set on each source.

2.3 The lifetime with post warranty service for IPM if operated by manufacturer is at least 10 years.

The post warranty service includes efficient repair and elimination of found defects in case IPM was disabled, testing, improvement and resetting of operational parameters and setting IPM to work during commissioning of the installation.

3  Supply kit
3.1 The information on supply kit is provided in Table 2.

Table 2

	Designation
	Name
	Quantity

	1 IP 02.00.00.000

   IP 02.00.00.000-01

   IP 02.00.00.000-02

   IP 02.00.00.000-03
	High voltage power supply

 IPM -25/15

IPM -25/22

IPM -15/15

IPM -9/15
	1 item

	2 IP 01.80
	High voltage connection cable
	1 item.

	3 IP 02 PS
	Passport
	1 item

	4 IP 02 ТО
	Technical description and operation guide
	1 item


4  Safety measures
4.1 According to way of protection against electrical shock IPM is referred to class 1 (GOST 12.2.007.0-75)
4.2 IPM is earthed in accordance with the system TN-C.

When mounted, the case of IPM must be connected with ground loop by means of cable with the cross section at least 16 mm2.

4.3 While implementing works connected with mounting, setting up and operation of IPM. Please, observe “The operation rules for consumers’ electrical installations”.

4

4.4 The brigade, implementing connection and maintenance of IPM must include at least 2 people, one of them must have at least the fourth qualification group in electrical security.

4.5 Disconnection of cable jack of IPM high voltage input is allowed only FIVE minutes after relief of supplying voltage.

4.6 The oil must be filled through the hole in the cover, which is designated for mounting of cartridge for dehydration to low levels on the inspection hole.

4.7 IT IS PROHIBITED:

- to repair the equipment alive;

- to switch off high voltage cable jack when power supply is on;

- to work with unearthed IPM;

4.8 Only personnel who studied technical description and operation guide for IP 02 TO is admitted to works on it.

5  Technical maintenance
5.1 Technical maintenance is carried out by maintenance personnel, who studied maintenance documentation and having at least the fourth qualification group in electrical safety.

5.2 To  guarantee continuous operation of IPM it is necessary (MONTHLY):

- to clean IPM from dust and dirt, to inspect exterior to find out occasional damage and debugging;

- to check oil level in IPM and absence of oil leakage through sealers;

- to check earthing;

- to rub inner surface of glass of high voltage outlet of IPM and glass of high voltage cable with a tampon wetted in spirit;

Attention!!!
The works on high voltage connection cable (connection and disconnection) must be carried out at temperature not lower – (minus) 15°С.

- to test oil for electrical durability. When discharge voltage decreases to 30 kW for the standard interval, the oil is to be replaced;

- if the silica gel in dehydration patron darkens, it must be replaced.

5


_939642580

